This document subject to change without notice.

www.matrixcabling.com

Introduction

This installation guide has been produced to assist the Matrix Partners with the best installation

practices for the Matrix Structured Cabling System. The Matrix Structured Cabling system meets the

component performance and configuration requirements of EN50173 for the Class of performance

desired. The location is based on a Class 1 environment in terms of M, I, C, E. The design of the

cabling system and containment solution into which it is to be installed should be compliant with the

requirements of the EN50174 and EN50310 standards.

CONTENTS

Planning

Before you start, prepare to start.

- l Have you got the cabling system design mapped onto the layout of the space?

- l Do you have the correct materials ordered against the Bill Of Materials estimated to complete the project?

- l Has the fire stop solution been approved?

- l Do you need any specialist training or product support from Matrix?

- l Are the deliveries scheduled to match the installation plan?

- l Are there any site inductions required? If so, when are these held?

- l Is the area to be handed over to you for your installation? If so, in what condition? Will you be required to run a ‘Permit to

- Work’ scheme for you and other trades?

- l Is there a clean, dry, secure storage area allocated for your materials?

- l Are there any special precautions to observe for site Health and Safety?

- l Are the method statements and COSH statements for the installation, termination and testing approved?

- l Do you have a change control process and reporting scheme?

- l Do you need to notify the site with the names or identification for your staff?

- l Is the labelling method, scheme, style, colour agreed and approved by the client?

- l Is the test equipment serviceable and to specification?

- l Is there a headroom performance requirement from the tested cabling?

- l Have you agreed how to deal with a star pass, (ie. marginal results)

- l Do you have access to power outlets for testers, laptops etc?

On site

- l Is the containment installed in the correct place and to the right specification?

- l Are you holding daily briefings for the site operatives?

- l Is there any temporary fire stopping required during the installation phase?

- l Is there any difference between the reality of the site and the plans?

- l Are there any access restrictions or other trades working in the same areas at the same time?

- l Is the earthing and electrical system installed?

- l Is there restriction on the use of mobile phones or walkie-talkies?

Site Environment Classification

The environments where cabling is to be installed are classified to cover the different conditions under which the cabling is required to operate. Conditions which may affect the cabling performance are used to determine the applicable environmental classification. Use the environmental classification to select the components. The same classification is used to determine the appropriate containment and installation techniques.

The local environment along the channel is classified for each M, I, C, or E group, and the classification of an environment is determined by the most demanding parameter within the M, I, C or E group. With regard to temperature, the local environment is considered to be the operating temperature of the cabling.

The considerations for:

- Mechanical rating include shock/bump, vibration, crush, impact, bending, flexing and torsion

- Ingress rating include particulate ingress, immersion

- Climatic and Chemical rating include humidity, rate of change of temperature, solar radiation, damaging chemical concentration

- Electromagnetic rating include electrostatic discharge, conducted radio frequency, magnetic field

All twisted pair copper cabling supplied by Matrix for normal indoor use is designed and classified to perform in a Class 1 environment (M1, I1, C1, E1). Most indoor office and data centre environments fall within the Class 1 environment (M1, I1, C1, E1).
If you have a specification requirement which is beyond Class 1 use you must consult with Matrix technical support for guidance on containment and product selection.

Containment and Cable Routing

Power and Data Separation

Local and national safety regulations may require different separation or segregation distances. Separation and segregation for safety must take precedence over all other requirements. To reduce the risk of noise disturbing the data flowing in copper twisted pair cables, Matrix recommends following the requirements set out in the latest issue of EN50174; these are summarised below. The more stringent requirement (greater distance) shall take precedence.

Essentially there are two ways of mitigating the effects of noise disturbing the transmission of data in a copper twisted pair cable; one way is to separate by distance the twisted pair cabling from the noise source, using air to attenuate any noise; the other way is to provide a barrier between the noise source and the twisted pair cabling using a grounded barrier to attenuate the noise.

The factors to consider are:

- Environment

- Type of containment

- Performance of cable type

- Application being supported

- Construction of power cable

- Scale of power source

- Proximity to the power cable

When all of this is calculated you get a separation recommendation.

Environment: 
All twisted pair copper cabling supplied by Matrix for normal indoor use is designed and classified to perform in a Class 1 environment M1, I1, C1, E1.

Containment: 
No barrier or no metallic barrier (typically wall trunking or open ladder), open metallic (typically basket but not ladder), perforated metallic (typically slotted tray) and solid metallic (typically 1.5mm wall steel conduit).

Cable Style: 
The performance of the cable and connector set is provided by the manufacturer. The applications to be supported will be the determination factor that provides the Classification for the cabling system chosen.

Power Cable: 
An assumption is made that power cables will provide a high degree of self cancellation for any noise carried if they are constructed with a live, neutral and earth bound together in a common sheath. If individual tails are used (separate unbound conductors) then power cable is to be treated as a noise hazard.

Power Scale: 
How many power cables are present or likely to be installed? Classification for power cabling is based on the qualification of a single phase 230 Volt, 20 Amp circuit. Three phase power is to be treated as three times a single phase. For circuits which are more than 20A treat as multiples of 20A. Lower voltage AC or DC power cables must be treated on their current rating, e.g. a 100A 50V DC cable is equivalent to 5 off 20A cables.

A = S x P

A (Final Separation Distance) = S (Basic Separation Distance) x P (Power Cabling Factor)

|  |  | Cable Management System |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Segregation Classification | Cable Performance | None (or Non-metallic) | Open metallic containment | Perforated metallic containment | Solid metallic containment |
| d | Class FA | 10mm | 8mm | 5mm | 0mm |
| c | Class D or E or EA F/UTP | 50mm | 38mm | 25mm | 0mm |
| b | Class D or E or EA U/UTP | 100mm | 75mm | 50mm | 0mm |
| a | Coaxial | 300mm | 225mm | 150mm | 0mm |

S - Basic Separation Distance

P - Power Cabling Factor

| Quantity of Circuits | P - Power Cabling Factor |
| --- | --- |
| 1 to 3 | 0.2 |
| 4 to 6 | 0.4 |
| 7 to 9 | 0.6 |
| 10 to 12 | 0.8 |
| 13 to 15 | 1.0 |
| 16 to 30 | 2.0 |
| 31 to 45 | 3.0 |
| 46 to 60 | 4.0 |
| 61 to 75 | 5.0 |
| > 75 | 6.0 |

Zero Segregation - Conditional Relaxation of Requirement

Where the requirements in specific EMI conditions do not apply, no segregation distance is required between power and data where:
Power - Single Phase, Total power = 32A, Power conductors contained in overall sheath or twisted, taped, bundled together
Data Cable - Segregation Classification is “b”, “c” or “d” in an E1 environment classification of EN 50173

Separation requirements for specific EMI sources

| Source of Disturbance | Minimum separation | Note |
| --- | --- | --- |
| Fluorescent Lamps | 130mm | a |
| Neon lamps | 130mm | a |
| Mercury vapour lamps | 130mm | a |
| High-intensity discharge lamps | 130mm | a |
| Arc welders | 800mm | a |
| Frequency induction heating | 1000mm | a |
| Hospital equipment |  | b |
| Radio transmitter |  | b |
| Television transmitter |  | b |
| Radar |  | b |

NOTE

A) The minimum separations may be reduced provided that appropriate cable management systems are used or product suppliers

guarantees are provided

B) Where product suppliers guarantees do not exist, analysis shall be performed regarding possible disturbances e.g. frequency range,

harmonics, transients, bursts, transmitted power, etc.

Overhead and Under Floor Containment Fill Ratio

Cable trays, basket, ladder racking and other containment should be filled on day one:

- To accommodate a day one minimum calculated spare fill of 20%

- Up to a maximum of 150mm (6 in) cable depth for solid floor containment.

The spare capacity requirement is to allow room for future expansion, and to facilitate additions and removal of cables once the building becomes operational

NOTE: A calculated fill ratio of 50% will physically fill the entire containment due to spaces between cables, and random placement.

Picture shows a cable tray that is full of cable which equals a 50% fill ratio

PIC?

Example - What is the minimum width of a 75mm deep cable tray supporting 1000 cables, each with a diameter of 5.5mm?

Area of one cable = (cable diameter)2 x π
                                                      4

Area of one cable = (5.5)2 x 3.14 = 23.75mm2
                                              4

Area of 1000 cable = (5.5)2 x 3.14) x 1000 = 23746mm2
                                                         4

Multiply this occupied area by 1.2 to give 20% over size for day two expansion

Usable area or Area required within cable tray (50% fill) = cable tray width x cable tray depth
                                                                                                                                      2

1000 cables = (23746mm2) x 1.2 = cable tray width x 75mm
                                                                                     2

Minimum width of cable tray = 759.9mm

Heating Effects

Energy losses from within cabling will be translated into generation of heat. There are many factors which accumulate to create this

effect. The installer needs to be aware that the temperature rise in the cabling at these points can be in the order of 10oC or higher when

all of these factors come together. The temperature rise created is greatest where:

- the cabling is managed into large bundles

- and/or there are a large number of simultaneous users

- and/or cabling is run into constricted spaces such as at wall penetrations

- and/or the cabling is required to support higher energy applications / PoE applications.

These heating effects can be mitigated by:

- reducing the bundle size

- loosening the bundle ties at points of constriction

- distributing the high energy use across different cable bundles

Cable Installation

From the cabling system design and floor plans make a cable pulling schedule. Map the pulling schedule onto the floor plans.

- Identify the labels and cable ID so that temporary labelling can be applied.

- It may be faster, cheaper and more accurate to print two sets of the final cable labels, using one set for installation purposes and then replacing them after testing is completed. This will avoid unsightly ‘Pen Marks’ on the cable.

- Ensure that for each group of finished labels they are aligned and attached so they are readable from the same direction.

- If the installation is a mixture of copper and fibre optic cabling install the copper cabling first.

- Plan the occupation of cabling in the containment and along the route so that crossovers are eliminated and entry points into and exits from the containment are not congested.

- In any cable run where the cable is to be pulled the run should contain no more than two 90o bends. If more than two 90o bends are required or the sum of all angles is greater than 180o then there must be more pull points along the cable run where the cable is able to be managed in and out of the containment.

- Respect the installation bend radius of the cable. Never exceed the recommended maximum pulling load of the cables.

- Determine the pulling in points which will cause damage to the cable, though sharp edges or bends tighter than the installation bend radius.

- Apply any protection to the containment where damage to the cable sheath may occur. Consider using cable installation aids.

- Bundle size should be kept to a minimum.

- Maximum bundle size is 24 for 4 pair twisted copper cables.

- Smaller bundles make better use of limited containment space.

- With mixed length cables in a cable run always pull in the longest length cables first.

- Secure the stack of cable boxes or reels using a pulling frame or cable stands to hold the packaging in place.

- Pulling force must be respected. Maximum pull force for a single, or bundle of cables, is 110 N (25 lbf ).

- Avoid any cable kinks and maintain proper bend radius control during cabling pulling. If any kinks should occur, kinked cable should be removed and replaced.

- For safety, only use cable jacks and pulling frames which are designed for and fit for purpose.

- Always control the rate at which cables are pulled off the drum.

- Take great care over the management of cable drum.

- Hook and eye cable fixings are preferred.

- If nylon type zip ties are used, cutting off long ends may cause the creation of razor sharp edges; do not over tighten.

- No deformation, marking or compression of cable jacket is allowed.

- Acclimatise the cables to the location where they are to be installed, minimum 2 hours.

- Refer to the specification sheet for the installation and operating temperature ranges for the cables being installed.

- The recommended installation temperature range is 0o – 60oC (32o – 140o F). Avoid pathways exposed to extreme thermal cycling.

- Remember that for some outdoor cabling there may be a minimum installation temperature.

- Do not install copper cabling or optical fibre cabling with a metallic strength member outdoors when there is a thunder or lightening storm about.

- Only use approved lubricants and pulling gels for the cable type being installed.

- For external installations seal the ends of all cables with a water tight product before installation.

| Part Number | Description | Diameter | During Installation - Bend Radius | Installed - Bend Radius |
| --- | --- | --- | --- | --- |

Earthing, Grounding and Bonding

Unless you are a qualified and competent electrical person leave the connection of the earthing wire onto the electrical system to the electrical trade.

The best type of earthing conductor used to provide a signal earth connection is a flat braided strap. Flat is best because it offers a greater surface area and braided straps because impedance is affected by length and braid offers many different routes and therefore lengths of conductor for the unwanted signals to flow along. If you use a solid core conductor to provide an earth strap you can improve this by adding a second, different length, earth conductor to reduce the possibility of an impedance issue resisting the passage of the unwanted signals.

Do not coil an earthing conductor around a screwdriver to make it look neat and tidy, you are forming a coil which can restrict the transmission of signals.

It is best practice to connect the earth stud in a cabinet onto a separate earthing bar located in the cabinet. It is recommended that the bar is provided with four or more attachment points for equipment earths to be connected onto. This is because if all of the equipment earths are run back to the earth stud then for safety reasons the electrical supply must be disconnected every time a new piece of equipment is added or removed from the cabinet.

When installing a piece of equipment which requires a signal earth, always install the equipment, then attach the earth connection, then connect up the power.

ESD (Electrostatic Discharge) can kill equipment. When installing equipment into a cabinet or frame always use an ESD strap connected between you and the cabinet.

Each earthing conductor must be grounded onto a clean, purposeful earthing point. Use an approved cleaning method and bonding gel to protect the joint from oxidisation.

Do not daisy chain earthing conductors; the only exception to this is where there is a run of metallic cable containment when each
length must be grounded onto the next.

Example of Cabinet Earthing

DIAGRAM!

Example of Cabinet Earthing

Cabinet earthing pic...

The best practices for communications rooms and data centres recommend provision of an equipotential earthing grid or MESH-BN (a bonding network in which all associated equipment frames, racks and cabinets and usually the DC power return conductor, are bonded together as well as at multiple points to the Common Bonding Network).

This grid is used to earth all of the metallic components (frames, cabinets, floor tiles and pedestals, cable containment, etc) providing:

- a reliable signal reference

- adequate immunity from electromagnetic interference carried by the earthing network

Each cabinet and frame must be provided with an earthing conductor made back to either the MESH-BN or home run back to the main communications grounding bar within the room. For some installations this may be the electrical earthing bar in the main power distribution board.

Cabinets and Frames

- Install the cabinets and frames in the pre assigned positions.

- Check alignment of any containment with the cable entrances (for power and data) to the cabinet.

- Apply temporary labels to identify the location.

- Secure the cabinets and frames to the solid floor and/or wall to provide stability when loaded with equipment and cabling.

- Install any baying or joining components.

- Attach the earthing kit to all cabinet and frame components.

- Connect the main earthing conductor.

- Does the site require blanking panels for airflow management in the cabinets and/or frames?

The layout for the inside of each cabinet should be determined in the overall site design. As with a lot of new designs there are great pressures on the space available within the cabinets and frames. As a general rule for laying out a cabinet, begin at the top with the patch panels starting with optical fibre panels then copper panels. The top most position in a block of patch panels should be reserved for a horizontal wire manager, then there should be no more than two patch panels of 1U height followed by another (or closing) horizontal wire manager. On high density frames the front fingers of the vertical wire manager provide the support for patch cords so there is not the same level of requirements for horizontal wire managers. Horizontal raceways will be required to facilitate shortest routing between patch panel outlets.

- When installing panels and wire managers use all of the securing and fixing holes provided.

Patch Panels

Termination procedures at the patch panel:

- Feed cables from both sides of the panel

- Maintain acceptable bend radius levels

- Do not kink cables

- Do not do up cable ties so tightly as to deform the cable in any way

To enhance wire management in the back of the panel, it is recommended that a strain relief bar is mounted to the rack. Along the strain relief bar use hook and eye cable ties for additional cable management.

Termination procedures for the punch down patch panel:

- Follow installation instruction sheet

- Outer cable jacket should be trimmed to be as close as possible to point of termination

- Last twist should be no further than 13 mm (0.5 inches) from the point of termination.

Wall Boxes and Desk Outlets

For a duplex, twin outlet presentation, choose a back box that complies with the minimum bend radius of the cable.

If metal GOP boxes or metal face plates are used, ensure that there is a grounding facility / earthing lug and a suitably sized earth wire connection, with sufficient cable to earth the box and lid.

Colour code

The colour code or punch down followed by Matrix for all of their cabling system components is the T568B format.

pic

Diagram

Testing

Twisted Pair Copper

This section describes and sets out the requirements for Class D (Cat 5e) and Class E (Cat 6) balanced twisted pair copper Permanent Link testing and Channel testing for the Matrix warranty. There are additional testing requirements set out in the cabling standards for Class EA (Cat 6A) product sets such as ANEXT sampling which is addressed in Appendix A, otherwise the processes outlined here are equally applicable to Class EA (Cat 6A) product sets.

The preferred test equipment is a Fluke DTX 1800. Alternatives are Fluke DTX 1200 or DSP 4300.

Permanent Link Testing

The test set must be fitted with a set of:

- Fluke Permanent Link Adapter PLA1 with Personality Module PM06 (RJ45)

OR

- Fluke Permanent Link Adapter PLA2 (RJ45)

Channel Testing

The test set must be fitted with a set of Fluke Channel test heads.

IMPORTANT:

- The Channel Test Heads and Personality Modules must have completed less than 5000 tests. Once the Fluke Channel Test Heads and Personality Modules have undertaken 5000 tests they must be replaced with new Channel Test Heads and Personality Modules and the old ones removed from site.

- The test set must be within 12 months of calibration.

- Tests must be run with Graphs Stored enabled and HDTDR / HDTDX recorded for all tests.

- Calibration of the Permanent Link Adapters shall be carried out in accordance with the recommendations of Fluke using a DTXCAL or DSPCAL as appropriate and on replacement of a Personality Module.

- All Channel Test Heads, Personality Modules or Personality Module tips must be frequently inspected for damage or undue wear.

- At least one set of Fluke calibration tools DSPCAL, DTXCAL must be kept on site at all times during the project installation and testing phases. NOTE: this may give you an improvement in XTALK and RL results.

- Power frequency must be set to 50Hz.

- Limits database and software must be as per the product set under test and Matrix warranty requirement.

- The test limits for Matrix are CENELEC EN50173 series including all latest amendments, modified by the copper cable type under test (Class D, Class E, etc). If there is any doubt for installed cabling regarding which component performance specification to be used, confirmation should be sought from the client or Project Manager and referred back to Matrix for approval under their warranty scheme.

- Installers should budget and schedule for replacement of Channel Test Heads, PLA2 tips and Personality Modules. The replacement rate may be lower than recommended or required depending on wear and condition of the test equipment on site.

- Matrix will not accept any Permanent Link or Channel test results, where Channel Test Heads and Personality Modules have been used beyond the maximum of 5000 tests.

Tester Log Sheet

A tester and test set component usage log sheet must be kept with each test set and maintained by the operator of the test set. The

- tester log must record the components within the test set including:

- test set ID (serial numbers from all major components)

- test cord ID

- test head serial numbers (PLA and Channel Head)

- calibration status (date of calibration for each component)

- component usage (number of tests executed)

- operator ID (name and company)

Replacement of ALL Copper Reference Test Cords is mandatory when they have completed 100 tests or earlier if damage is present on

the test cord connectors.

At The Start of Each Day

- Check that the batteries are fully charged

- Check all results from the previous day have been off loaded onto a laptop

- Perform a visual check on the condition of the tester components for wear or damage

- Fill out the tester log sheet and confirm all the tester components and leads are within their usage limits

- Plug the designated main end Channel Head or PLA into the main end of the tester

- Plug the designated remote end Channel Head or PLA into the remote end tester

- Enter operator name site and starting cable ID to be tested

NOTE: Every 6 Months (immediately after calibration and then +6 months) run DSPCAL or DTXCAL set up on the PLA heads

For Each Project

- Enter the NVP for the cable obtained from the product specification sheet

- Enter the performance level specification for the Channel or Permanent Link to be tested CENELEC EN50173 Class D, Class E, etc.

Recommendations

- Perform a basic wire map test with a Mod Tap (wire map), or similar, before using the Fluke tester to fault find

- Have a laptop computer on site with the latest version of Fluke Linkware installed

- Identify Main and Remote on the Channel adapters and PLA with a permanent ink pen or label ID system

Matrix requires a copy of the test results in Fluke software (flw) and PDF format.

Each report will be stored by Matrix.

The Installer will be provided with a copy of the Channel Warranty documentation and certificate within 4 weeks of submission and

acceptance.

Labels and Administration

Matrix recommends using the Sharpmark? labelling solutions and templates. All Matrix panels, outlets and faceplates are supported with predefined label layouts and formats.

An administration system is required by the network owner to organise and control connections and operation of their network and the associated support infrastructure. A full and detailed labelling scheme should be agreed before the start of the installation. As a minimum this will require labels and identifiers being applied to cables, outlets, panels, cabinets and frames. For larger or more complex installations a more comprehensive administration and labelling scheme is required. Best practices include labelling of items such as:

- Bonds – functional earth

- Cabinets, racks and frames

- Cables - both ends

- Closures

- Pathways

- Spaces

- Termination points including joints

- Cords/jumpers - both ends

Operation & Maintenance

The O&M manual or documentation handed over to the client at the end of the job is a record of what has been provided with

information about the products, how they have been implemented and the testing records.

An O&M package should include:

- As built drawings showing:

- date of installation completion

- site identity / location identity

- location of outlets

- identity of outlets

- location of cabinet and frames

- identity of cabinet and frames

- If required with occupancy and capacity of cabinet and frames

- pathways used

- If required identity of pathways

- If required with occupancy and capacity of pathways

- fire stopping

- If required identity of fire stop with occupancy and capacity

- Grounding / earthing points

- If required identity of grounding / earthing and connections

- Details of the product set used throughout the installation including:

- product part numbers

- product data sheets

- label format and typeface

- Bill Of Materials

- Summary test result sheets for all outlets and tested components

- CD of the detailed test results

- Copy of the Fluke Linkware used to view the results

- Details of the test equipment used to certify the performance of the cabling system

- Calibration certificates for the test equipment used

- Details of the test methods used

- Warranty certificates from Matrix

- Details of any routine or periodic maintenance requirements including cleaning methods and materials

- Contact details for the installer

Permanent Link Description

A Permanent Link is defined as the cabling between two outlets (or three outlets if a Consolidation Point (CP) or Local Distribution Point (LDP) is used) but excludes any patch cords.

A Permanent Link, is the fixed cabling, to which equipment and work area cords are added to complete the channel (see diagram below).

Physically the Permanent Link includes cable and outlets (possibly presented in a patch panel). Where a CP or LDP is required in the Permanent Link the CP or LDP to Outlet cord and the outlet are to be included in the Permanent Link measurement and testing. There are limits imposed within the standards for key electrical parameters such as insertion loss, XTALK, RL, ELFEXT, etc. The horizontal PL must take into consideration all elements necessary to configure the operational channel, which has a limit of 100m (305ft).

Channel Description

A channel is defined as the “up to 100m” connection between two active components.

Physically the channel includes horizontal cable outlets (possibly a patch panel), Interconnect (fan out cables) and any cross connect (patch cords), equipment or work area patch cords. There are limits imposed for key electrical parameters such as Attenuation, XTALK, RL, ELFEXT, etc, the channel is not limited to a maximum of 4 connectors or junctions. However should a channel configuration require more than 4 connectors then approval must be given, at design stage, by Matrix for their warranty support.

Testing of a channel can take two forms:

- Confidence test where the patch cords are removed or replaced following the test

- Full test where the final configuration is tested and left in place

A channel test serves to validate either conformity with the generic cabling standards or application support.

The term “Reference Cord” is defined here as a new Matrix patch cord that will only be used for up to 100 tests. After 100 tests the Reference Cord must be destroyed and replaced with another new Matrix Reference Cord.

Before a Channel test is performed all components in the Permanent Link must have been configured and validated for component compliance.

Marginal or star passes on all other criteria are to be treated as failures.